# Integration Test Plan for DeltaV & Event‑Driven Architecture

## 1 Scope and objectives

1.1 Verify that DeltaV process values, batch events, alarms and user actions flow reliably through HighByte, HiveMQ and the unified namespace to Ignition, PI, the event database and the data lake.
1.2 Confirm that metadata (timestamps, quality flags, sequence numbers) and contextual attributes (unit, batch ID, tag name) are preserved end‑to‑end.
1.3 Exercise security controls, high‑availability features and time‑synchronisation across all components[1].
1.4 Employ a mix of exploratory (“unscripted”) and scripted testing aligned with FDA’s risk‑based CSA guidance[2].

## 2 Test environment

2.1 Install DeltaV controllers, professional‑plus station, continuous historian and event chronicle.
2.2 Deploy HighByte Intelligence Hub connected to DeltaV OPC DA/UA and event chronicle; configure Sparkplug B models and topics.
2.3 Deploy HiveMQ cluster with TLS and certificate‑based authentication.
2.4 Deploy Ignition gateway subscribed to MQTT topics; configure alarming and audit trail.
2.5 Deploy PI historian with DeltaV interfaces; deploy event database and data‑lake ingestion pipeline.
2.6 Synchronise all systems to a common NTP/PTP time source.

## 3 Test cases

### 3.1 Basic data flow verification

3.1.1 Objective – Confirm that HighByte collects process tags (e.g., temperature, pressure) and publishes them via MQTT with correct metadata.
3.1.2 Method – Select a small set of DeltaV tags; trigger changes in DeltaV; observe in HiveMQ, Ignition and PI.
3.1.3 Expected result – Tags appear in the unified namespace with correct value, timestamp, engineering units and quality flags; HiveMQ broker logs show receipt at QoS 1/2; Ignition displays live trends; PI records time‑series points.

### 3.2 Batch/event propagation

3.2.1 Objective – Verify that batch start/stop, unit procedure and phase events propagate from DeltaV’s event chronicle[3] to HighByte and onward.
3.2.2 Method – Start a dummy batch in DeltaV; execute a few phases; finish the batch; capture batch ID and event timestamps.
3.2.3 Expected result – Corresponding “batch start,” “phase start/end” and “batch end” events with correct IDs and timestamps are published; Ignition displays them; PI creates an event frame with proper hierarchy; event DB records the events and correlates them to the batch ID.

### 3.3 Alarm and safety event handling

3.3.1 Objective – Ensure that process alarms and safety events are delivered to all consumers.
3.3.2 Method – Simulate a high‑high temperature alarm in DeltaV and a safety trip; acknowledge and clear the alarm in Ignition.
3.3.3 Expected result – Alarm set, acknowledged and cleared events appear in MQTT topics with sequence numbers; Ignition alarm summary shows proper priority and timestamps; PI event chronicle stores the alarm; acknowledgement is recorded in the audit trail.

### 3.4 Audit trail and command flow

3.4.1 Objective – Confirm that operator actions (logins, parameter changes, manual overrides) are captured and that control commands can be executed through the unified namespace.
3.4.2 Method – Log into Ignition using a test account; change a setpoint via Ignition; verify that the change propagates to DeltaV and that the audit log records user ID, old/new values and time.
3.4.3 Expected result – MQTT control topic publishes the command with proper authentication; HighByte forwards it to DeltaV; DeltaV’s event chronicle records the change; audit logs in Ignition and event DB reflect the action.

### 3.5 Security and authentication

3.5.1 Objective – Validate TLS and certificate‑based authentication on MQTT and OPC UA, and confirm role‑based access.
3.5.2 Method – Attempt connections with valid and invalid certificates; attempt to publish to restricted topics; attempt to subscribe without permissions.
3.5.3 Expected result – Valid connections succeed; invalid certificates or unauthorized topics are denied; audit logs capture failed access attempts.

### 3.6 High‑availability and recovery

3.6.1 Objective – Verify that redundant components behave as expected during failure and recovery.
3.6.2 Method – Deliberately shut down one HiveMQ node; observe client failover; disconnect the network segment between HighByte and HiveMQ; observe store‑and‑forward and backlog processing; restart components.
3.6.3 Expected result – Clients reconnect to surviving brokers with no message loss; HighByte queues data and flushes when connectivity is restored; PI and event DB backfill data correctly.

### 3.7 Exploratory error‑seeking testing

3.7.1 Objective – Perform unscripted scenario testing as recommended by FDA CSA[2].
3.7.2 Method – Testers explore unusual sequences: rapidly toggle a control mode between manual and auto; simulate network latency or out‑of‑order messages; attempt to delete or modify an event in the event DB; attempt to circumvent an alarm acknowledgement.
3.7.3 Expected result – System behaves gracefully: invalid operations are rejected; audit trails record attempts; alarms are re‑latched if conditions persist; no data loss or corruption occurs.

## 4 Documentation and evidence

4.1 Record test objectives, methods, results, and any anomalies.
4.2 Capture objective evidence such as screenshots, message logs, PI queries and audit trail records.
4.3 Document any deviations and corrective actions.
4.4 Summarise findings and determine whether additional scripted tests are needed once risk classifications are defined.

[1] DeltaV Zones

https://www.emerson.com/documents/automation/product-data-sheet-deltav-zones-deltav-en-56272.pdf

[2] Computer Software Assurance for Production and Quality Management System Software

https://www.fda.gov/media/188844/download

[3] White Paper: DeltaV Event Chronicle

https://www.emerson.com/documents/automation/white-paper-deltav-event-chronicle-en-55962.pdf